SAMPLE SPECIFICATIONS

MODEL: AZTEC 30 - 1000 HP

1.0 Specification Overview

2.0 Structural Specifications

3.0 Connections

4.0 Boiler Trim

5.0 Factory Firetest

_________________________________________________________________

AZTEC 2-Pass Steam Boiler, 30-1000 HP, 15 PSI Section IV, 150-300 PSI Section I.

The size and location of all connections, steam-disengaging area, furnace volume and steam storage volume can be found on Superior Boiler Works Form CAT5SB (dated 11-18-97).

Contact your local insurance carrier and State Boiler Inspector for the current insurance and code requirements.

Please contact Superior Boiler Works factory if you need any assistance in completing the specification.

1.0   Specification Overview

  - The boiler shall be a 2-pass Aztec dryback boiler manufactured by Superior Boiler Works, Model No.________________________.  The boiler shall not have less than five square feet of A.S.M.E. heating surface, measured on the fireside, per rated boiler horsepower.

1.2	The boiler is to be mounted on a structural steel base with 	a forced draft burner 	and burner controls.  The boiler is 	to be designed, constructed and tested in 	accordance with the latest edition and addenda of the A.S.M.E. Boiler and 	Pressure Vessel Code and shall be registered with the National Board of Boiler 	and Pressure Vessel Inspectors.

1.3 	The boiler shall be designed for              PSI steam 	with an operating pressure of            	in accordance with 	the latest edition and addenda of Section (I), or (IV), of 	the A.S.M.E. Boiler & Pressure Vessel Code.

1.4 	The steam boiler shall be completely pre-assembled and firetested at the factory 	to check construction, controls and combustion characteristics of the unit.

1.5 	Boilers smaller than 300 HP are to be constructed to meet 	the requirement of 	CSD-1; boilers 300 HP and larger are to comply with the requirements of 	NFPA8501.  The complete 	packaged boiler shall be listed as a unit by 	Underwriters 	Laboratories and shall bear the Underwriters label.

2.0 	Structural Specification

2.1 	The steam boiler is to be designed to produce a steam quality of 99% at all firing 	rates.

2.2 	The furnace is to be located in the bottom third of the boiler to provide for 	maximum heat transfer while being in contact with the coolest boiler water.

2.3	All Section I boilers over 350 square feet are to have a furnace of the Morrison 	corrugated design and shall have a furnace volume of not less than ________ 	cubic feet.

2.4 	All tubes are to have a minimum wall thickness of .105" and have an OD of 2-	1/2".  The tubes on a Section I boiler are to be attached to the tubesheets by 	flare rolling and then beading the tubes to the tubesheet.  The tubes on a Section 	IV boiler are to be attached by flare rolling.

  - Turbulators shall be factory installed in all tubes to enhance the convective heat transfer coefficient.

2.6 	The boiler tubesheets on Section I boilers Model 5-625 and larger are to be a 	minimum of 3/4" thick.

2.7 	The boiler shall be mounted on a heavy structural steel base with extended 	runners on the front to provide burner support and protection.

2.8 	The rear saddles are to be slotted to provide for movement  when the boiler 	expands from a cold to a hot condition.

2.9 	All heating surfaces must be fully accessible for inspection and cleaning without 	disturbing the burner equipment.  All boilers over 350 square feet of heating 	surface are to have a 15" diameter rear access plug in the rear door.  Boilers over 	3750 square feet of heating 	surface are to have a 19" diameter rear access plug.  	The plug is to be gasketed and supplied with handles for ease or removal.  The 	plug is also to be equipped with a Pyrex observation port and shutter assembly 	for the observation of the burner flame.  The shutter assembly is to have a 1/8" 	tapping for the field connection of a manometer.

2.10	The rear turnaround area, tubesheets, and refractory are to 	be fully accessible 	when the rear door is opened.  The rear turnaround area is to house the refractory 	blocks and bridge.  The blocks and bridge are to be manufactured from a 	high 	quality castable insulating refractory equal to Plibrico LWI24.  The rear door 	refractory is to be poured from the same material as the refractory blocks and is 	to be "one piece construction" with no baffles.  The refractory is to be held in 	place with anchors welded to the refractory side of the rear door.

2.11  	The rear door is to be supported by an extra heavy-duty davited hinge that is 	capable of supporting the door when it is being opened or shut.  The hinge is to 	be positioned so that the rear door will open to the (right) (left) when viewed 	from the burner end.

  - The front doors are to be insulated with a 1" thick ceramic fiber blanket.  The insulating blanket is to have a K factory of .44 and is to be coated with a hardener to prevent erosion from the flue gases.  Front doors on  boilers over 350 square feet in heating surface are to be of the davited design.

2.13 	All doors are to be held in place by lugs that are secured by replaceable brass 	nuts.  The doors are to be sealed with a gas tight, non-proprietary ceramic fiber 	rope with a minimum density of 20 lbs. per cubic ft. and a continuous use limit 	of 1800 degrees F.

2.14	All necessary handholes and manholes shall be provided in accordance with the 	A.S.M.E. Code.  Provide two additional handholes to improve the ease of 	waterside inspection and cleaning located in the front tubesheet near the bottom 	of the boiler on either side of the furnace.

2.15	The front and rear tubesheets must be fully accessible for inspections or cleaning 	when the front doors or rear door is open.  Fuel lines, linkages, and electrical 	connections shall not impede opening of the doors.

2.16	The boiler shell is to be insulated with two inch thick, eight pound per cubic foot 	density mineral wool with a K factor of .27.  The insulation is to be held in place 	by bands and then covered with a 22 gauge phosphate coated galvanized steel 	jacket.  All opening in the jacket are to have trim rings.

2.17	The entire boiler is to be painted with a high temperature, 	400 degrees F 	minimum, silicone based enamel.  The front and rear doors are to be sand blasted 	before painting and the jacket is to be primed with a vinyl wash primer before 	painting.

3.0	Connections

3.1	The boiler is to have   (Qty)     (Size)   bottom blowdown 	connections.

3.2	Section IV boilers are to be supplied with one factory piped and installed slow 	opening blowdown/drain valve. Section I boilers are to be supplied with one 	factory piped 	and installed quick opening blowdown valve per boiler 	blowdown connection, and one slow opening valve per boiler.  The piping is 	to be documented on the Manufacturer's Data Report.

  - The boiler is to be equipped with two lifting eyes.

3.4	Two   (Size)   feedwater connections on the horizontal center line shall be 	provided, one on each side of the boiler.  Each connection shall be furnished 	with an 	internal baffle.

3.5	One set of feedwater valves (one gate valve and one check valve) the same size 	as the boiler feedwater connection is to be factory piped and installed on one of 	the feedwater	connections. The piping is to be documented on the 	Manufacturer's Data Report Form.

3.6	A   (Size)   flue gas connection shall be located at the front of the boiler on the 	top centerline.  The stack shall be designed for easy attachment of the exhaust 	flue by allowing for a slip connection.  The flue gas connection will be designed 	to support a minimum of 2,000 lbs dead weight.  The stack shall have a 1/2" 	connection for a stack thermometer.

3.7	A one-inch surface blowdown connection complete with a dip tube shall be 	provided.

3.8	One set of surface blowdown valves (a gate type shutoff valve and a calibrated 	flow control valve) are to be  factory piped and installed on the boiler.  The 	piping is to be documented on the Manufacturer's Data Report.

3.9 	The steam connection will be a   (Size)    class (300#  Section I) (150# Section  	IV).

3.10	Boilers over 500 square feet in fireside heating surface are to be supplied with a 	low fire hold connection located in the bottom third of the shell.

4.0	Boiler Trim

4.1	A float type primary low water cut-off and pump control shall be provided with 	gage glass, ball check gage glass valves, try-cocks and a ball type water column 	blowdown valve.

  - A probe type secondary low water cut-off shall be provided.

4.3	A high limit control with manual reset shall be provided in addition to the 	operating control.

4.4	A firing rate controller if the burner is low-hi-low or modulating shall be 	provided.

4.5	Relief valves set at a minimum of 17% higher than the operating pressure of the 	boiler, but no higher than the boiler design pressure shall be provided.

4.6	A pressure gauge with an inspector's test cock shall be provided.

5.0	Factory Firetest

5.1	The factory firetest shall be a complete functional test conducted at 10 PSIG 	(Sect. IV) or 100 PSIG (Sect. I) and, at a minimum, is to consist of filling the 	boiler with water and operating the burner throughout its complete range of 	operation. Additionally, all of the components wired into the boiler safety 	control circuit are to be tested by simulating a failure condition.  A copy of the 	firetest report is to be included in the manual.

5.2	Upon completion of the factory firetest, the boiler shall be cooled and 	hydrostatically tested and the boiler external piping documented.  The unit shall 	be ready for installation and final connection of water, steam, fuel, 	blowdown, 	electrical and flue.