Scotch Marine Steam Boilers

MODEL: SUPER SEMINOLE 70 - 1800 HP

1.0 Specification Overview

2.0 Structural Specifications

3.0 Connections

4.0 Boiler Trim

5.0 Burner Control

6.0 Exhaust Gas Analysis

7.0 Factory Firetest

_________________________________________________________________

SEMINOLE 3-Pass Steam Boiler, 70 - 1800 HP, 150 PSI Section I.

The size and location of all connections, steam-disengaging area, furnace volume and steam storage volume can be found on Superior Boiler Works CATX6SB (dated 3-03).

Contact your local insurance carrier and State Boiler Inspector for the current insurance and code requirements.

Please contact Superior Boiler Works if you need any assistance in completing the specification.

1.0   Specification Overview

  - The boiler shall be a 3-pass Super Seminole wetback boiler with XID tubes manufactured by Superior Boiler Works, Model No.X6-5-2000-S15-W-G (400HP).  The boiler shall not have less than five square feet of A.S.M.E. heating surface, measured on the fireside, per rated boiler horsepower.

1.2	The boiler is to be mounted on a structural steel base with a forced draft burner and burner controls.  The boiler is to be designed, constructed and tested in accordance with the latest edition and addenda of the A.S.M.E. Boiler and Pressure Vessel Code and shall be registered with the National Board of Boiler and Pressure Vessel Inspectors.

1.3 	The boiler shall be designed for 150 PSI steam with an operating pressure of            in accordance with the latest edition and addenda of Section I of the A.S.M.E. Boiler & Pressure Vessel Code.

1.4 	The steam boiler shall be completely pre-assembled and 	firetested at the factory to check construction, controls 	and combustion characteristics of the unit.

1.5 	Boilers smaller than 300 HP are to be constructed to meet 	the requirement of CSD-1; boilers 300 HP and larger are to 	comply with the requirements of NFPA8501.

2.0 	Structural Specification

2.1 	The steam boiler is to be designed to produce a steam 	quality of 99% at all firing rates.

2.2 	The furnace is to be located in the bottom third of the 	boiler to provide for maximum heat transfer while being in 	contact with the coolest boiler water.

2.3 	All boilers constructed to Section I of the A.S.M.E. Code are to have a furnace of the Morrison corrugated design and shall have a furnace volume of not less than 115.7 cubic feet.  The flue gas turnaround area is not to be included in calculating furnace volume.

2.4 	All tubes are to have a minimum wall thickness of .105" and 	have an OD of 2-1/2".  First pass of tubes is of XID type (extended internal heating surface).  The tubes on a Section I boiler are to be attached to the tubesheets by flare    rolling and then beading the tubes to the tubesheet.  The tubes on a Section IV boiler are to be attached by flare rolling.

  - All tubesheets on Section I boilers are to be a minimum of 3/4 of an inch to insure a tight seal between the tube and the tubesheet.

2.6 	The boiler shall be mounted on a heavy structural steel 	base with extended runners on the front to provide burner 	support and protection.

2.7 	The rear legs are to be slotted to provide for expansion 	when the boiler goes from a cold situation to a hot 	situation.

2.8 	All heating surfaces must be fully accessible for 	inspection and cleaning without disturbing the burner 	equipment.  A 17" diameter access opening complete with a 	gasketed plug and a Pyrex observation port and shutter 	shall be provided to allow for access into the turnaround 	and furnace.  The plug is to be equipped with handles and 	the shutter assembly is to have a 1/8" tapping for the 	field connection of a manometer.

2.9 	All necessary handholes and manholes shall be provided in 	accordance with the ASME Code.  Provide two additional 	handholes, to improve the ease of waterside inspection and 	cleaning, in the front tubesheet near the bottom of the 	boiler on either side of the furnace.

2.10  The front and rear tubesheets must be fully accessible for inspections or cleaning when the front or rear doors are open. Opening of the doors, two in front and two in back, is not to be impeded by any fuel lines, door plates, baffles, linkage or electrical connections.  The doors are to have davited hinges and are to be insulated with a 1" thick ceramic fiber blanket. The insulating blanket is to have a R factor of .44 and is to be coated with a hardener to prevent erosion from the flue gases. All doors are to be held in place by lugs that are secured by replaceable brass nuts.  The doors are to be sealed gas tight with non-proprietary ceramic fiber rope with a minimum density of 20 	lbs. per square foot and a continuous use limit of 1800ºF.

  - The boiler shell is to be insulated with two inch thick, eight pound per cubic foot density mineral wool with a R factor of .27.  The insulation is to be held in place by bands and is to be covered with a 22 gauge phosphate coated galvanized steel jacket.  All openings in the jacket are to have trim rings.  The area on the rear tubesheet under the access doors is to be insulated with the same insulation and covered with 22 gauge phosphate coated galvanized steel jacket.

2.12  The entire boiler is to be painted with a high temperature, 	500 degrees F minimum, acrylic silicone based paint.  The  	front and rear doors are to be sand blasted before painting  	and the jacket is to be primed with a vinyl wash primer  	before painting.

2.13	All boilers are to have a 12" x 16" manway located along 	the top centerline of the boiler to facilitate waterside 	cleaning and inspection.  The top of the boiler furnace is  	to be visible when the manway cover is removed from the 	boiler shell.

3.0	Connections

3.1	The boiler is to have (2)1 ½” bottom blowdown connections.

3.2	Section I boilers are to be supplied with one factory piped 	and installed quick opening blowdown valve per blowdown 	connection, and one slow opening valve per boiler.  The 	piping is to be documented on the Manufacturer's Data 	Report.

3.3	The boiler is to be equipped with two lifting eyes.

3.4	Two 2”feedwater connections on the horizontal center line shall be provided, one on each side of the 	boiler.  Each connection shall be furnished with an 	internal baffle.

3.5	One set of feedwater valves (one gate valve and one check valve) the same size as the boiler feedwater connection is to be factory piped and installed on one of the feedwater connections. The piping is to be documented on the Manufacturer's Data Report.

3.6	A 24” flue gas connection shall be located at the front of the boiler on the top centerline.  The stack shall be designed for easy attachment of the exhaust flue by a flange connection. The flue gas connection will be designed to support a minimum of 2,000 lbs of dead weight.  The stack shall  have a 1/2" connection for a stack thermometer.

3.7	A one-inch surface blowdown connection complete with a dip 	tube shall be provided.

3.8	One set of surface blowdown valves (a gate type shutoff 	valve and a calibrated flow control valve) is to be factory 	piped and installed on the boiler.  The piping is to be 	documented on the Manufacturer's Data Report.

3.9 	The steam connection will be a 6” class (300# Section I).

3.10	The boiler is to be supplied with a low fire hold 	connection located in the bottom third of the shell.

4.0	Boiler Trim

4.1	A float type primary low water cut-off and pump control 	shall be provided with gage glass, ball check gage glass 	valves, try-cocks and a ball type water column blowdown 	valve.

4.2	A probe type secondary low water cut-off shall be provided.

4.3	A high limit with manual reset shall be provided in 	addition to the operating control.

4.4 	A firing rate controller shall be provided.

4.5 	Provide relief valves set at a minimum of 17% higher than 	the operating pressure of the boiler, but no higher than 	the boiler design pressure.

  - A pressure gauge with an inspector's test cock shall be provided.

5.0	Burner Control Specification

5.1	The burner controller is to be a microprocessor based fuel air ratio control with integral flame safeguard supervision. The controller must have the following approvals; UL, ULc, FM and conform to NFPA 85.

5.2	The combustion control system must be a dedicated electronic fuel air ratio controller. PLC (Programmable Logic Controllers) will not be acceptable.

5.3	The controller must be housed within a steel enclosure and protected to NEMA 4 standard. The controls enclosure should be finished using industrial powder coat.

5.3	All combustion and burner information must be visually displayed continuously. The display should be a backlit ¼” VGA screen with dynamic display capability.

5.4	Operation of servomotors and variable speed drives shall be checked by means of feedback signals. Incorrect operation shall initiate an error message and shut the system down.

5.5	The controller must be able to control up to 4 separate positioning servo motors and 2 variable speed drives. The controller must be able to control servomotors to an accuracy of 0.1 degrees angular and the variable speed drives to within +/-1Hz.

5.6	The controller shall provide an easily programmable and flexible means of optimising combustion quality throughout the load requirement range of the boiler/burner unit. It should be possible for a suitably qualified person to make alterations to the way in which the unit is commissioned without the need for a separate computer.

5.7	The control unit should ensure that the required boiler pressure is maintained to within 1.5psi. The controller shall have an integral PID control that can only be adjusted via password protection. Both “Required” (setpoint) and “Actual” (steam pressure) shall be displayed.

5.8	The combustion controller must include the following features:

- 4 separate fuel programs.

- Single point change capability.

- Low fire hold facility & Manual modulation facility.

- User definable optimum ignition position.

- Trim on air damper or Variable speed drive channel.

- Fuel flow metering and display.

- Password protection for all safety related options and parameters.

- Infrared Communications port for upload and download of commission data.

- 4-20mA or 0-10volt input for external control of firing rate

- 4-20mA or 0-10volt output confirming firing rate.

- Local/remote control selection without burner shut down.

- Full lead/lag (sequencing) capability.

- Time clock facility.

- Lockout record, showing where unit has locked out and when such lockout’s have been reset. These lockouts should be held in memory for operator reference.

- FGR start facility to allow unit to start safely prior to flue gases being added.

- Second set point facility.

5.9	The positioning motors for fuel valves and air damper control should be capable of the torque inflicted upon them. The enclosures and casings must be manufactured from steel and powder coated. Plastic positioning motors will not be acceptable.

5.10	All other peripheral devices e.g. UV detectors and sensors must also not be enclosed within plastic housings.

5.11	By means of a data transfer interface module, all the operational data stored within each of the combustion control systems shall be monitored at all times. It should be possible to retrieve information via the following methods:-

- RS232 connection for local link.

- RS422 connection for long distance link

- The facility shall also exist to retrieve the information via Modem connection.

The information shall be retrievable in the form of MODBUS protocol for easy interface to plant master controls.

6.0	Exhaust Gas Analysis

6.1	The burner controller should operate in conjunction with an exhaust gas analyser to monitor and control the combustion gases. The analyser should individually measure and display 02, C02, C0, N0 and exhaust gas temperature to calculate boiler combustion efficiency. A calculated C02 value will not be acceptable.

6.2	At the same time as measuring these parameters the analyser should inflict minute corrections on the air damper position to ensure that the originally entered commissioning data is adhered to, irrespective of variations in stack pressure or barometric conditions.

6.3	The combustion control system shall be able to set user definable limitations for all the measured parameters of combustion. If any of these parameters are exceeded or fallen short of, an error/alarm shall occur to inform the plant operator/supervisor of a potential hazard.

6.4	The combustion control system shall be able to display visually on line values of emissions.

7.0	Factory Firetest

7.1	The factory firetest shall be a complete functional test conducted at 100 PSIG (Sect. I) and, at a minimum, is to consist of filling the boiler with water and operating the burner throughout its complete range of operation. Additionally, all of the components wired into the boiler safety control circuit are to be 	tested by simulating a failure condition.  A copy of the firetest report is to be included in the manual.

7.2	Upon completion of the factory firetest, the boiler shall be cooled and hydrostatically tested and the boiler 	external piping documented.  The unit shall be ready for installation and final connection of water, steam, fuel, 	blowdown, electrical and flue.